## Summary
Manifold Design Worksheet | [16 empty] | Project Name
- Enter Data Fields
| Number of Circuits |  | 1 |  |  |  |  | Antifreeze |  | 1 | [6 empty] | Factor | 1
[17 empty] | Average PD |  | #DIV/0! | gpm
|  | 0 | Loop Data | [6 empty] | Supply/Return Data | [6 empty] | #DIV/0! | #VALUE! | Adjusted Flow to Equal DP
| Ckt # | Design Flow | # of loops | Loop Diam | Loop Length | Loop DR | gpm/ loop | Ref gpm | Ref DP | S/R Length | S/R Diam | S/R DR | Ref gpm | Ref DP | Loop DP | S/R DP | Ckt DP | with Antifreeze | Flow gpm | % vs Design | gpm/ loop | Re
| 1 | [16 empty] | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on F8: Enter total equivalent length of pipe
Note on K8: Enter total equivalent length of pipe

## Data
Reference Flow (gpm) | [7 empty] | Reference Pressure Drop (Feet of Head/100' of Pipe)
Size | 7.4 | 9 | 11 | 13.5 | 15.5 | 17 |  | Size | 7.4 | 9 | 11 | 13.5 | 15.5 | 17
0.75 | 2.9 | 3.3 | 3.7 | 3.8 | 4.1 | 4.2 |  | 0.75 | 2.58 | 2.402 | 2.3075 | 2.122 | 2.0684 | 2.0301
1 | 4.5 | 5.2 | 5.7 | 6 | 6.5 | 6.6 |  | 1 | 1.944 | 1.8619 | 1.7314 | 1.651 | 1.6214 | 1.5656
1.25 | 7.2 | 8.2 | 9.1 | 9.6 | 10.3 | 10.5 |  | 1.25 | 1.491 | 1.3904 | 1.3182 | 1.2665 | 1.2218 | 1.1884
1.5 | 9.4 | 10.7 | 11.9 | 12.5 | 13.5 | 13.8 |  | 1.5 | 1.285 | 1.1785 | 1.123 | 1.0693 | 1.0441 | 1.0208
2 | 14.7 | 16.7 | 18.5 | 19.6 | 20.9 | 21.5 |  | 2 | 2.893 | 0.9059 | 0.8558 | 0.829 | 0.7906 | 0.782
3 | 32 | 36.3 | 40.2 | 42.6 | 45.4 | 46.6 |  | 3 | 0.6227 | 0.5764 | 0.5437 | 0.5274 | 0.5025 | 0.495
4 | 52.7 | 60 | 66.3 | 70.4 | 75.1 | 77.3 |  | 4 | 0.4609 | 0.4295 | 0.4036 | 0.3928 | 0.3749 | 0.3713
6 | 114.5 | 130 | 143.9 | 152.6 | 162.7 | 167.2 |  | 6 | 0.2944 | 0.273 | 0.2573 | 0.2499 | 0.2383 | 0.2352
8 | 194.4 | 220.5 | 244.4 | 258 | 276.8 | 284.2 |  | 8 | 0.2169 | 0.2008 | 0.1898 | 0.1827 | 0.1762 | 0.1737
Antifeeze Properties |  |  |  |  | % by Volume | Density lb/ft3 | Viscosity Centipoise | PD Factor
1 | Water (32 F Freeze Point) |  |  |  |  | 62.55 | 1.55 | 1
2 | 7.7% Methanol (25 F Freeze Point) |  |  |  | 7.7% | 61.88 | 2.15 | 1.0936
3 | 12.0% Methanol (20 F Freeze Point) |  |  |  | 12% | 56.63 | 2.7 | 1.1908
4 | 16.3% Methanol (15 F Freeze Point) |  |  |  | 16.3% | 61.35 | 3.3 | 1.2305
5 | 12.8% Propylene Glycol (25 F Freeze Point) |  |  |  | 12.8% | 63.38 | 1.9 | 1.0515
6 | 18.0% Propylene Glycol (20 F Freeze Point) |  |  |  | 18% | 63.68 | 3 | 1.187
7 | 23.0% Propylene Glycol (15 F Freeze Point) |  |  |  | 23% | 64.13 | 6.3 | 1.34
Pipe Inside Diameters
Size | 7.4 | 9 | 11 | 13.5 | 15.5 | 17
0.75 | 0.766 | 0.817 | 0.86 | 0.884 | 0.915 | 0.926
1 | 0.96 | 1.023 | 1.075 | 1.107 | 1.145 | 1.16
1.25 | 1.211 | 1.291 | 1.358 | 1.397 | 1.446 | 1.465
1.5 | 1.386 | 1.478 | 1.554 | 1.599 | 1.655 | 1.676
2 | 1.733 | 1.847 | 1.943 | 1.999 | 2.069 | 2.096
3 | 2.554 | 2.722 | 2.864 | 2.946 | 3.0484 | 3.0882
4 | 3.284 | 3.5 | 3.682 | 3.788 | 3.9194 | 3.9706
6 | 4.834 | 5.153 | 5.421 | 5.577 | 5.7702 | 5.8456
8 | 6.294 | 6.708 | 7.057 | 7.26 | 7.5121 | 7.6103
0.75 | 7.4
1 | 9
1.25 | 11
1.5 | 13.5
2 | 15.5
3 | 17
4
6
8